## Sheet1
Pressure Temperature Chart
Refrigerant: | R600A | R1234ZE | Engas M30 | R152A | Minus30EC | R134A | R1234YF | Minus30 | R290 | Engas M50 | R22 | Minus50 | R454C | R407C | Engas M20 | Engas M60 | R1270 | HC32 | R404A | Minus60 | R410A | R32 | R170 | R744
Temperature (°C): | Pressure (KPAG) (Avg bubble & dew for blend refrigerants): (figures in shaded grey are extrapolated)
-70 | -97 | -94 | -98.71 | -92 | -105 | -108 | -87 | -84 | -77 | -110.49 | -82 | -67 | -79.4 | -82 | -122.07 | -123.1 | -68 | -65.5 | -73 | -48 | -64 | -62 | 148.6 | 69.3
-66 | -95 | -92 | -92.83 | -89 | -96 | -100 | -85 | -79 | -71 | -93.37 | -76 | -59 | -73 | -76.5 | -99.98 | -100.44 | -60 | -57 | -66 | -36 | -54.5 | -52 | 195.4 | 171.1
-62 | -93 | -90 | -86.8 | -86 | -87 | -94 | -81 | -73 | -63 | -77.14 | -68 | -49 | -65.4 | -69.5 | -79.45 | -79.41 | -50 | -46 | -57 | -23 | -42.5 | -40 | 248.4 | 272.9
-58 | -91 | -87 | -80.39 | -82 | -78 | -87 | -76 | -67 | -54 | -61.24 | -59 | -38 | -56.3 | -61 | -59.77 | -59.28 | -39 | -34 | -46 | -7 | -28.5 | -25 | 308.3 | 374.7
-54 | -88 | -84 | -73.41 | -77 | -68 | -80 | -70 | -59 | -43 | -45.17 | -49 | -24 | -45.5 | -51 | -40.26 | -39.37 | -25 | -20 | -33.5 | 10 | -11.5 | -8 | 375.4 | 476.5
-50 | -85 | -79 | -65.65 | -70 | -58 | -73 | -63 | -49 | -31 | -28.42 | -37 | -9 | -32.5 | -38.5 | -20.31 | -19 | -10 | -3.2 | -18 | 31 | 8.5 | 12 | 450.5 | 581
-46 | -80 | -74 | -56.89 | -63 | -47 | -64 | -54 | -39 | -16 | -10.53 | -22 | 9 | -17.5 | -24.5 | 0.68 | 2.36 | 9 | 16 | 0 | 53 | 31.5 | 36 | 534 | 698.8
-42 | -75 | -67 | -46.93 | -55 | -35 | -55 | -44 | -26 | 0.5 | 8.95 | -5 | 29 | 0 | -7.5 | 23.27 | 25.33 | 29 | 38 | 20 | 79 | 59 | 63 | 626.4 | 831.2
-38 | -70 | -60 | -35.45 | -45 | -21 | -44 | -32 | -11 | 20 | 30.93 | 14 | 52 | 20.5 | 12.5 | 48.69 | 51.18 | 53 | 63 | 44.5 | 108 | 90.5 | 95 | 728.3 | 979.2
-34 | -63 | -50 | -22.58 | -33 | -5 | -32 | -18 | 5 | 42 | 54.28 | 37 | 78 | 43.5 | 35 | 75.22 | 78.11 | 80 | 91 | 71.5 | 141 | 126.5 | 131 | 840.3 | 1143.9
-30 | -55 | -39 | -7.82 | -20 | 12 | -17 | -2 | 24 | 67 | 80.69 | 63 | 107 | 71 | 61.5 | 105.21 | 108.55 | 111 | 123 | 103 | 177 | 168.5 | 173 | 963 | 1326.4
-28 | -50 | -33 | 0.33 | -12 | 22 | -9 | 7 | 34 | 80 | 95.12 | 77 | 123 | 86 | 76 | 121.59 | 125.17 | 128 | 140 | 120.5 | 197 | 191 | 196 | 1028.5 | 1424.7
-26 | -45 | -27 | 9.03 | -4 | 32 | 0.3 | 17 | 45 | 95 | 110.42 | 92 | 140 | 101.5 | 91.5 | 138.94 | 142.78 | 145 | 159 | 139 | 218 | 215.5 | 220 | 1096.9 | 1527.9
-24 | -40 | -20 | 18.29 | 4 | 43 | 10 | 27 | 57 | 110 | 126.61 | 108 | 158 | 118 | 109 | 157.3 | 161.4 | 164 | 180 | 158.5 | 239 | 241.5 | 247 | 1168.3 | 1636.2
-22 | -35 | -12 | 28.14 | 14 | 54 | 20 | 38 | 69 | 126 | 143.73 | 126 | 177 | 136.5 | 126.5 | 176.7 | 181.08 | 184 | 199 | 179.5 | 262 | 269 | 274 | 1242.7 | 1749.6
-20 | -29 | -4 | 38.61 | 24 | 66 | 31 | 50 | 82 | 143 | 161.81 | 144 | 197 | 155.5 | 145.5 | 197.18 | 201.86 | 205 | 220 | 201.5 | 286 | 298 | 304 | 1320.2 | 1868.3
-18 | -23 | 5 | 49.72 | 34 | 79 | 43 | 62 | 96 | 161 | 180.89 | 164 | 217 | 175.5 | 165.5 | 218.78 | 223.77 | 227 | 240 | 224.5 | 311 | 329 | 335 | 1400.9 | 1992.5
-16 | -16 | 14 | 61.5 | 45 | 92 | 56 | 75 | 111 | 180 | 201 | 184 | 240 | 197 | 187.5 | 241.54 | 246.85 | 250 | 267 | 249.5 | 337 | 362 | 368 | 1485 | 2122.4
-14 | -9 | 24 | 73.97 | 57 | 106 | 69 | 89 | 126 | 200 | 222.17 | 206 | 263 | 219.5 | 210.5 | 265.49 | 271.14 | 275 | 293 | 276 | 365 | 397 | 403 | 1572.3 | 2258
-12 | -1 | 35 | 87.16 | 70 | 121 | 84 | 104 | 143 | 222 | 244.45 | 229 | 287 | 244 | 234.5 | 290.68 | 296.68 | 301 | 319 | 303 | 394 | 433.5 | 440 | 1663.2 | 2399.6
-10 | 7 | 46 | 101.09 | 84 | 137 | 99 | 120 | 160 | 244 | 267.86 | 254 | 313 | 269.5 | 260.5 | 317.14 | 323.5 | 328 | 347 | 332.5 | 424 | 472.5 | 479 | 1757.5 | 2547.4
-8 | 16 | 58 | 115.8 | 98 | 154 | 116 | 137 | 178 | 267 | 292.45 | 279 | 339 | 296.5 | 287.5 | 344.91 | 351.66 | 356 | 376 | 363.5 | 455 | 513.5 | 520 | 1855.5 | 2701.4
-6 | 25 | 71 | 131.31 | 114 | 171 | 133 | 154 | 197 | 292 | 318.24 | 307 | 367 | 325 | 316 | 374.03 | 381.18 | 386 | 407 | 395.5 | 488 | 556.5 | 564 | 1957.2 | 2861.8
-4 | 35 | 85 | 147.65 | 130 | 189 | 151 | 173 | 216 | 318 | 345.28 | 335 | 397 | 354.5 | 346.5 | 404.54 | 412.11 | 417 | 439 | 429.5 | 523 | 601.5 | 610 | 2062.7 | 3028.9
-2 | 45 | 99 | 164.85 | 147 | 209 | 171 | 193 | 237 | 345 | 373.6 | 365 | 427 | 385.5 | 378.5 | 436.49 | 444.5 | 450 | 472 | 465.5 | 558 | 649.5 | 658 | 2172 | 3202.9
0 | 56 | 115 | 182.92 | 166 | 229 | 191 | 214 | 259 | 373 | 403.24 | 397 | 460 | 418.5 | 412.5 | 469.91 | 478.37 | 484 | 507 | 503 | 595 | 699.5 | 709 | 2285.4 | 3383.8
2 | 67 | 131 | 201.91 | 185 | 250 | 213 | 236 | 282 | 403 | 434.24 | 430 | 493 | 453.5 | 448 | 504.85 | 513.77 | 520 | 544 | 543 | 634 | 752.5 | 762 | 2402.9 | 3572
4 | 79 | 148 | 221.84 | 205 | 272 | 236 | 259 | 306 | 434 | 466.64 | 465 | 528 | 489.5 | 485.5 | 541.34 | 550.75 | 558 | 582 | 584 | 675 | 808 | 818 | 2524.5 | 3767.5
6 | 92 | 167 | 242.75 | 227 | 295 | 261 | 283 | 331 | 466 | 500.47 | 501 | 565 | 527.5 | 525 | 579.43 | 589.35 | 597 | 622 | 627.5 | 716 | 866 | 877 | 2650.5 | 3970.7
8 | 105 | 186 | 264.65 | 250 | 320 | 286 | 309 | 357 | 500 | 535.77 | 539 | 603 | 568 | 566 | 619.16 | 629.6 | 637 | 663 | 672.5 | 760 | 927 | 938 | 2780.9 | 4181.7
10 | 119 | 206 | 287.58 | 274 | 345 | 313 | 335 | 385 | 535 | 572.58 | 579 | 642 | 610 | 609 | 660.58 | 671.56 | 680 | 707 | 720.5 | 805 | 990 | 1003 | 2915.9 | 4400.9
12 | 134 | 228 | 311.57 | 299 | 372 | 342 | 363 | 413 | 572 | 610.94 | 621 | 684 | 653 | 654.5 | 703.73 | 715.25 | 724 | 752 | 770 | 852 | 1056.5 | 1070 | 3055.6 | 4628.3
14 | 150 | 250 | 336.65 | 325 | 399 | 372 | 393 | 443 | 610 | 650.89 | 664 | 727 | 699 | 702 | 748.59 | 760.76 | 770 | 799 | 822 | 901 | 1126 | 1141 | 3200.1 | 4864.4
16 | 166 | 274 | 362.84 | 353 | 428 | 403 | 424 | 474 | 650 | 692.47 | 710 | 771 | 747 | 752.5 | 795.32 | 808.07 | 818 | 847 | 876 | 951 | 1198.5 | 1215 | 3349.5 | 5109.5
18 | 183 | 299 | 390.19 | 382 | 458 | 436 | 456 | 506 | 692 | 735.73 | 757 | 818 | 797 | 804 | 843.9 | 857.28 | 868 | 898 | 932.5 | 1004 | 1274 | 1292 | 3504.2 | 5363.8
20 | 201 | 325 | 418.72 | 413 | 489 | 470 | 490 | 540 | 735 | 780.7 | 807 | 866 | 849 | 858.5 | 894.42 | 908.39 | 919 | 950 | 991 | 1058 | 1353 | 1372 | 3664.1 | 5627.7
22 | 220 | 353 | 448.45 | 445 | 522 | 507 | 525 | 575 | 780 | 827.42 | 858 | 916 | 903.5 | 915 | 946.83 | 961.49 | 973 | 1005 | 1052.5 | 1114 | 1435 | 1456 | 3829.7 | 5901.8
24 | 239 | 381 | 479.43 | 479 | 555 | 544 | 562 | 611 | 827 | 875.94 | 911 | 968 | 959.5 | 974.5 | 1001.25 | 1016.63 | 1029 | 1062 | 1115.5 | 1172 | 1521 | 1543 | 4001 | 6186.4
26 | 260 | 412 | 511.69 | 515 | 590 | 584 | 601 | 649 | 875 | 926.25 | 967 | 1022 | 1018 | 1036 | 1057.7 | 1073.8 | 1086 | 1120 | 1182 | 1232 | 1610 | 1634 | 4178.5 | 6482.4
28 | 281 | 443 | 545.24 | 551 | 627 | 626 | 641 | 688 | 926 | 978.49 | 1025 | 1078 | 1079.5 | 1100.5 | 1116.25 | 1133.08 | 1146 | 1181 | 1251 | 1294 | 1702.5 | 1729 | 4360.1 | 6790.5
30 | 303 | 476 | 580.14 | 590 | 665 | 669 | 683 | 729 | 978 | 1032.63 | 1085 | 1136 | 1143 | 1167.5 | 1176.9 | 1194.53 | 1208 | 1244 | 1322 | 1358 | 1799 | 1827 | 4548.6 | 7112.3
32 | 327 | 511 | 616.4 | 631 | 704 | 714 | 726 | 771 | 1032 | 1088.73 | 1147 | 1196 | 1209 | 1237 | 1239.77 | 1258.15 | 1272 | 1309 | 1396 | 1425 | 1898.5 | 1930 | 4743.4 | 7535.7
34 | 351 | 547 | 654.06 | 673 | 744 | 761 | 771 | 814 | 1088 | 1146.87 | 1212 | 1258 | 1277.5 | 1309.5 | 1304.87 | 1324.04 | 1338 | 1377 | 1473 | 1493 | 2002.5 | 2036 | 4944.5 | 7980.4
36 | 376 | 585 | 693.17 | 717 | 787 | 811 | 819 | 860 | 1146 | 1207.04 | 1279 | 1322 | 1348.5 | 1385 | 1372.25 | 1392.22 | 1406 | 1447 | 1553 | 1564 | 2110 | 2147 | 5152.2 | 8425.9
38 | 403 | 624 | 733.75 | 763 | 830 | 862 | 868 | 906 | 1206 | 1269.28 | 1348 | 1389 | 1422 | 1463 | 1441.94 | 1462.8 | 1477 | 1519 | 1635.5 | 1636 | 2221.5 | 2261 | 5366.6 | 8871.4
40 | 430 | 665 | 775.83 | 811 | 875 | 915 | 918 | 955 | 1268 | 1333.7 | 1420 | 1457 | 1498.5 | 1544.5 | 1514.01 | 1535.77 | 1550 | 1594 | 1721 | 1712 | 2337.5 | 2380 | 5588 | 9317
42 | 458 | 708 | 819.42 | 860 | 922 | 971 | 971 | 1005 | 1332 | 1400.32 | 1494 | 1528 | 1577 | 1628.5 | 1588.49 | 1611.18 | 1625 | 1671 | 1809.5 | 1789 | 2457 | 2504 | 5816.6 | 9762.5
44 | 488 | 753 | 864.59 | 912 | 971 | 1029 | 1026 | 1057 | 1399 | 1469.18 | 1571 | 1602 | 1659 | 1716 | 1665.49 | 1689.15 | 1703 | 1751 | 1900.5 | 1869 | 2581 | 2631 | 6052.5 | 10208
46 | 519 | 799 | 911.35 | 966 | 1021 | 1089 | 1083 | 1110 | 1468 | 1540.32 | 1650 | 1677 | 1744 | 1806 | 1745.05 | 1769.63 | 1783 | 1833 | 1995.5 | 1951 | 2709 | 2764 | 6295.9 | 10653.5
48 | 551 | 847 | 959.8 | 1023 | 1072 | 1152 | 1142 | 1166 | 1539 | 1613.77 | 1732 | 1755 | 1831 | 1899.5 | 1827.19 | 1852.77 | 1865 | 1918 | 2093.5 | 2036 | 2841.5 | 2901 | 6547.2 | 11099.1
50 | 584 | 897 | 1009.9 | 1081 | 1126 | 1217 | 1203 | 1223 | 1612 | 1689.67 | 1816 | 1836 | 1921.5 | 1996.5 | 1911.98 | 1938.6 | 1950 | 2006 | 2194 | 2123 | 2978.5 | 3042 | 6806.4 | 11544.6
52 | 618 | 949 | 1061.66 | 1142 | 1181 | 1284 | 1266 | 1282 | 1688 | 1767.94 | 1903 | 1919 | 2015.5 | 2096.5 | 1999.46 | 2027.19 | 2038 | 2096 | 2298 | 2213 | 3120 | 3189 | 7073.9 | 11990.1
54 | 653 | 1003 | 1115.25 | 1205 | 1237 | 1354 | 1331 | 1342 | 1766 | 1848.74 | 1993 | 2005 | 2111.5 | 2200 | 2089.77 | 2118.53 | 2128 | 2190 | 2405.5 | 2305 | 3265.5 | 3340 | 7349.9 | 12435.6
56 | 690 | 1059 | 1170.53 | 1270 | 1296 | 1427 | 1399 | 1405 | 1847 | 1932.12 | 2086 | 2094 | 2211 | 2307 | 2182.88 | 2212.77 | 2221 | 2286 | 2516.5 | 2400 | 3416.5 | 3496 | 7634.6 | 12881.2
58 | 728 | 1117 | 1227.7 | 1338 | 1356 | 1502 | 1469 | 1470 | 1930 | 2018.08 | 2181 | 2185 | 2313.5 | 2417.5 | 2278.91 | 2309.95 | 2316 | 2385 | 2630.5 | 2497 | 3572 | 3658 | 7928.3 | 13326.7
60 | 768 | 1177 | 1286.7 | 1408 | 1419 | 1580 | 1541 | 1536 | 2015 | 2106.74 | 2280 | 2279 | 2419.5 | 2531 | 2377.88 | 2410.12 | 2414 | 2487 | 2747.5 | 2598 | 3732 | 3824 | 8231.2 | 13772.2
70 | 986 | 1511 | 1610.91 | 1798 | 1759 | 2015 | 1937 | 1900 | 2485 | 2592.19 | 2815 | 2795 | 2996.5 | 3156 | 2920.02 | 2958.74 | 2943 | 3046 | 3388.5 | 3142 | 4606.5 | 4738 | 9893.9 | 15999.8
80 | 1243 | 1903 | 1987.63 | 2257 | 2152 | 2532 | 2397 | 2318 | 3031 | 3155.16 | 3425 | 3392 | 3660 | 3878 | 3548.96 | 3595.13 | 3543 | 3693 | 4121 | 3760 | 5611 | 5794 | 11830.8 | 18227.4
90 | 1541 | 2360 | 2422.64 | 2793 | 2602 | 3143 | 2925 | 2796 | 3663 | 3808.85 | 4116 | 4088 | 4413.7 | 4702.5 | 4282.27 | 4337.44 | 4217 | 4444 | 4951 | 4381 | 6753 | 7004 | 14082.9 | 20455.1
100 | 1885 | 2885 | 2920.83 | 3413 | 3114 | 3857 | 3524 | 3338 | 4384 | 4560.18 | 4889 | 4881 | 5262.3 | 5635.5 | 5126.6 | 5192.18 | 4966 | 5045 | 5881 | 5103 | 8039 | 8376 | 16697.1 | 22682.7
110 | 2281 | 3483 | 3488.82 | 4122 | 3694 | 4691 | 4199 | 3944 | 5209 | 5425.62 | 5746 | 5792 | 6209.6 | 6681.5 | 6103.52 | 6181.48 | 5792 | 5898 | 6915 | 5857 | 9474 | 9920 | 19725.8 | 24910.3
120 | 2735 | 4160 | 3488.82 | 4928 | 4349 | 5658 | 4953 | 4625 | 6149 | 6420.26 | 6689 | 6834 | 7258.2 | 7844 | 7231.94 | 7324.68 | 6696 | 6842 | 8053.7 | 6643 | 11063 | 11646 | 23227.8 | 27137.9
130 | 3257 | 4917 | 4860.49 | 5836 | 5085 | 6775 | 5787 | 5382 | 7217 | 7561.92 | 7719 | 8022 | 8409.9 | 9127 | 8534.71 | 8645.15 | 7679 | 7882 | 9298.5 | 7446 | 12809 | 13559 | 27268.7 | 29365.5
Boil (0KPAG): | -12.4 | -19 | -28.094 | -25.3 | -32.7606 | -26.4 | -29.4 | -35.1506 | -42.5 | -43.7925 | -41.1 | -48.0288 | -45.6 | -43.6 | -46.126 | -46.4284 | -47.8 | -49.227 | -46.2 | -55.5876 | -51.4 | -52.6 | -88.6 | -78.5
Critical temp: | 135 | 109.4 |  | 113 |  | 101 | 94.7 | 112 | 97 |  | 96 | 94 | 88.5 | 87 |  |  | 92 |  | 73 |  | 71.3 | 78 | 32.17 | 31
Averaging index: | R600A | R1234ZE | Engas M30 | R152A | Minus30EC | R134A | R1234YF | Minus30 | R290 | Engas M50 | R22 | Minus50 | R454C | R407C | Engas M20 | Engas M60 | R1270 | HC32 | R404A | Minus60 | R410A | R32 | R170 | R744
Air Conditioning | 283.44 | 448.6 | 545.6768 | 557.2 | 625.56 | 631.32 | 643.48 | 686.24 | 922.92 | 975.2016 | 1023.52 | 1073.48 | 1079.4 | 1103.36 | 1112.0516 | 1128.7448 | 1140.08 | 1176.04 | 1249.34 | 1284.96 | 1702.24 | 1730.92 | 4331.176 | 6934.32
Fridges | 179.6154 | 295.5769 | 381.5569 | 377.9615 | 446.7692 | 430.2308 | 448.1923 | 493.9231 | 675.4615 | 717.9788 | 740.8462 | 797.7692 | 780.8462 | 789.9615 | 823.4658 | 836.485 | 846.0385 | 875.7692 | 912.6923 | 976.8846 | 1249.3077 | 1268.1154 | 3417.35 | 5300.6346
Freezers | 121.3056 | 211.8889 | 285.5392 | 278.8611 | 340.0833 | 318.7028 | 336.6667 | 378.5833 | 526.2778 | 562.065 | 573.75 | 629.1944 | 605.7361 | 609.6389 | 647.8756 | 658.5525 | 666.3056 | 691.9444 | 713.4722 | 782.9167 | 982.9722 | 998.0833 | 2827.5583 | 4336.725
Enter temperature: | -49.227 |  |  | Info & Disclaimer:
Refrigerants: | Pressure (kPa): | Boil (0kPag): |  | www.hydrocarbonconspiracy.info
R600A | -83.1276 | -11.6425 |  | Facebook: "Hydrocarbon Conspiracy"
R1234ZE | -78.5219 | -19.0814 |  | Please check the main PDF document and other resources!
Engas M30 | -64.0415 | -28.094 |  | My technical research is based on much analysis of publicly available data, but isn’t endorsed by any of the hydrocarbon gas manufacturers.
R152A | -69.3842 | -25.009 |  | Not endorsed by the hydrocarbon refrigerant manufacturers.
Minus30EC | -56.1116 | -32.7606
R134A | -71.0847 | -26.0801
R1234YF | -61.2272 | -29.5816
Minus30 | -47.4629 | -35.1506
R290 | -27.5601 | -42.1659
Engas M50 | -25.0632 | -43.7925
R22 | -33.9357 | -40.8617
Minus 50 | -5.1129 | -48.0288
R454C | -29.8662 | -42.0061
R407C | -36.1501 | -40.4085
Engas M20 | -16.3528 | -46.126
Engas M60 | -14.989 | -46.4284
R1270 | -6.2365 | -47.8223
HC32 | 2.077e-05 | -49.227
R404A | -14.8869 | -45.9324
Minus 60 | 32.1536 | -55.5876
R410A | 12.5645 | -51.5909
R32 | 16.3578 | -52.3113
R170 | 465.8332 | -86.4558
R744 | 560.0665 |  | Error found when entering extreme temperature input data for R744, and will be updated in the next update.